## Summary
CG260-16 Installation Offers'
26 Nov, 2020
Summary for Installation of 5 X CG260-16 |  |  |  |  | CSD |  |  | Summary in USD ($)
ITEM | DESCRIPTION |  | UNIT | QTY | Unit Cost | Total Amount
1 | Custom made Sound proofed enclosure; o Paint o Attenuation o Air-intake / outtake + motorized louvres o Ventilation fan o Piping’s; exhaust, cooling line; fuel o Cable tray; On skid o Control Panel o Internal Lighting: o Cable trays + accessories o Air condition o Power and control cable; On skid o Junction Boxes + Earthen Bus for the Container |  | Lots | 5 | 87712015.99 | 438560079.95 |  | 1096400.1999
2 | Supply of SWG , Transformer and panels + shelter for both SWG and Control panel |  | Lots | 1 | 171740329.13 | 171740329.13 |  | 429350.8228
3 | Electro-mechanical installation |  | Lots | 1 | 154850357.8 | 154850357.8 |  | 387125.8945
SUB-TOTAL | [5 empty] | 765150766.88 |  | 1912876.9172
Exchange rate
[7 empty] | Naira | NGN 400
[7 empty] | Dollar | 1

## Sound Proof Enclosure
Customized Solution Department
Power System Division
Quotation
Subject: |  | Sound Proof Enclosure
Date: |  | 2019-09-06
Project: |  | CG260-16 ¦ QG045-BM-AM-19
Referring to the above mentioned project, please find our technical offer for Sound proof enclosures for CG260-16 Gensets.
1- Scope of Supply:
| Qty | Description
| 1 | Custom made Drop over Sound proofed enclosure suitable for CG260-16 genset with total dimensions L X W X H, 20.0 X 4.7 X 4.5 meters
2-General Description:
Paint : |  | The complete container will be finish painted, interior and exterior with Polyurethane paint. Color shall be Pure white . The floor will be coated with gray or Black epoxy paint.
Attenuation |  | The inner wall of the enclosure shall be lined with mineral wool cladded with perforated sheet. Also sound baffles will be included at the air outtake side of the container.
Air Intake: |  | Intake and combustion air shall enter through Motorized louver sections. These will be installed in the back of the container and sized for the requirements of the installed genset. Also Hot air shall exit through Motorized Louvre sections at the outtake side.
Ventilation Fan: |  | Four(4) ventilation fan shall be installed in the Genset room as required by the Genset.
Cable access: |  | A load cable access area will be provided by the side of the container for easier load cable access.
Piping |  | The coolant line shall be properly routed to the radiator. The fuel inlet line shall be routed outside the enclosure with adequate flanges for customer interconnections. Also Exhaust pipes and the Air intake filter ducting shall be properly routed.
Air conditioner: |  | 1 X 1hp AC split unit wall mounted shall be included in the panel compartment.
Internal Lighting: |  | Lamps will be provided in the generator set compartment. These will be fluorescent type 2x20 Watt, high quality type, warm white colour, and installed in lighting fixture, safety guard. One lighting switch and one socket will be installed at each entrance door
Control Cables interconnection: |  | Flexible control cables for on-skid interconnection with terminations accessories.Including interconnetion between Genset and auxiliaries
Power Cables interconnection: |  | Power cables for on-skid interconnection with terminations accessories.Including interconnetion between Alternator and GLF
Cable Trays: |  | Supply of Galvanized cable trays with accessories
Access doors: |  | Gasketed access doors .
All doors are equipped with steel hinges and latches with provisions for locking.
2- Terms and conditions:
| Price: | All prices quotes are in Nigerian Naira, excluding all taxes.
| Terms of payment: |  |  | 100% upon delivery.
| Validity: |  | This offer is valid for 30 days
| Warranty: |  | Warranty period is ONE year against defective material and faulty workmanship from the date of delivery to the warehouse
| Delivery: |  | Delivery date is Eight weeks for fabrication of the enclosure and five weeks after receiving the units. All referenced to the order date.
3- Price For one Enclosures:
| Enclosure PRICE: |  |  | 80712015.99 |  | NGN
| Packaging at site cost: |  |  | 7000000 |  | NGN
| TOTAL PRICE: |  |  | 87712015.99 |  | NGN

## Transformer & SWG
MANTRAC NIGERIA LTD.
#2 Billingsway Oregun Industrial Estate Lagos
Tel/Fax: 01-2716300
CLIENT: | QG061-BM-AM-19
TITLE: | Installation of 5 x CG260-16
LOCATION:
DATE: | 9 Dec, 2019
ATTN:
QUOTATION FOR THE SUPPLY OF TRANSFORMER , SWG AND PANEL
S/n | Description | Unit | Quantity | Unit Rate | Total Cost
1 | SUPPLY OF SWG , NGR & TRANSFORMER
a | SM6 630A Switchgear comprising of; 06 x Incomer 630A 05 x Outgoing 630A Accessories | Lots | 1 | 120867777.7 | 120867777.7
b | Supply of 1250kva 11kv / 415auxillary step- down transformer | Nos | 1 | 12639093 | 12639093
c | Supply of 6Mva 11kv / 415 step- down transformer | Nos | 5 |  | 0
d | Synch control panel | Lots | 1 | 12184653 | 12184653
e | ATS + Mcc Panel for pumps and other LV equipment | Lots | 1 | 10969333.33 | 10969333.33
f | SWG shelter custom made [ L=12m, W = 4.0m, H=4.0m] | Nos | 1 | 15079472.1 | 15079472.1
g | Synch panel shelter custom made [ L=12m, W = 4.0m, H=4.0m] | Nos | 1
| TOTAL |  |  |  | 171740329.13

## EM Installation
MANTRAC NIGERIA LTD.
#2 Billingsway Oregun Industrial Estate Lagos
Tel/Fax: 01-2716300
CLIENT: | QG061-BM-AM-19
TITLE: | Installation of 5 x CG260-16
LOCATION:
DATE: | 26 Nov, 2020
ATTN:
QUOTATION FOR THE INSTALLATION OF 5 X CG 260-16
S/n | Description |  | Unit | Quantity | Unit Rate | Total Cost
1 | LOGISTICS SCOPE.
a | Delivery of the New 5 x CG260-16 |  | Nos | 5
b | Delivery of 5 x Kva Step-Up Transformer |  | Nos | 5
c | Supply + Positioning of the Gen-Sets, Step-Up Transformer |  | Lot | 5
d | Delivery of SGW panel + Control panel |  | Lots | 1
2 | MV POWER CABLES GENSET
a | 3 x 150mm 11kv, XLPE from Gen-set 1 to SWG incomer 1 |  | Mtrs | 25 | 50300 | 1257500
b | 3 x 150mm 11kv, XLPE from Gen-set 2 to SWG incomer 2 |  | Mtrs | 25 | 50300 | 1257500
c | 3 x 150mm 11kv, XLPE from Gen-set 3 to SWG incomer 3 |  | Mtrs | 25 | 50300 | 1257500
d | 3 x 150mm 11kv, XLPE from Gen-set 4 to SWG incomer 4 |  | Mtrs | 35 | 50300 | 1760500
e | 3 x 150mm 11kv, XLPE from Gen-set 5 to SWG incomer 5 |  | Mtrs | 45 | 50300 | 2263500
3 | NGR POWER CABLES
a | 1 x 95mm 11kv, XLPE from Gen-set 1 to NGR 1 |  | Mtrs | 10 | 10700 | 107000
b | 1 x 95mm 11kv, XLPE from Gen-set 1 to NGR 2 |  | Mtrs | 10 | 10700 | 107000
c | 1 x 95mm 11kv, XLPE from Gen-set 1 to NGR 3 |  | Mtrs | 10 | 10700 | 107000
d | 1 x 95mm 11kv, XLPE from Gen-set 1 to NGR 4 |  | Mtrs | 10 | 10700 | 107000
e | 1 x 95mm 11kv, XLPE from Gen-set 1 to NGR 5 |  | Mtrs | 10 | 10700 | 107000
4 | MV POWER CABLES FOR TRANSFORMER
a | 3 x 150mm 11kv, XLPE from SWG to Transformer 1 | Xformer -1 | Mtrs | 25 | 50300 | 1257500
b | 3 x 150mm 11kv, XLPE from SWG to Transformer 2 | Xformer -2 | Mtrs | 25 | 50300 | 1257500
c | 3 x 150mm 11kv, XLPE from SWG to Transformer 3 | Xformer -3 | Mtrs | 25 | 50300 | 1257500
d | 3 x 150mm 11kv, XLPE from SWG to Transformer 4 | Xformer -4 | Mtrs | 35 | 50300 | 1760500
e | 3 x 150mm 11kv, XLPE from SWG to Transformer 5 | Xformer -5 | Mtrs | 45 | 50300 | 2263500
f | 3 x 35mm 11kv, XLPE from SWG to Auxilary Transformer | Aux - Xformer | Mtrs | 30 | 19100 | 573000
5 | BLACK START GEN-SET
a | Supply of 4 x 185mm armoured cable from Gen- ATS panel |  | Mtrs | 30 | 49650 | 1489500
b | Cable lugs and glands |  | Nos | 1 | 25000 | 25000
c | 7 x 2.5mm2 control cable (signaling ) |  | Mtrs | 100 | 2510 | 251000
6 | TERMINATION & TESTING OF MV CABLE
a | Meduim Volatge Cable • Supply all the needed test equipment to site • Lay the 11KV cables and termination of both cable ends for SWG, gen & xformer • Provide termination kits • Carry on Cable suitability test using VLF equipment and Megger.(insulation resistance test & High volatge test) • Provide a comprehensive report on completion. | GEN -SWG + SWG - Xformer | Lots | 1 | 5000000 | 5000000
b | Indoor 11KV single core termination kit; for 150 sqmm cable with 150/14 cable lugs ; Tinned copper braid, Mastic tape, Sillicne grease, Cleaning tissue, Abrasive strip, Glove, Breakout, Anti-tracking tube, Stress contral tube , Rain shed, Lug sealing tube, Outer jacket sleeve tube, Worm drive clips, Stress contral mastic, Dual wall tube (black + red), Stell armour case. |  | Lots | 12 | 275000 | 3300000
7 | CONTROL CABLE FROM NEW GEN TO CONTROL PANEL
a | 2 x 4mm2 control cable- (DC signal) |  | Mtrs | 500 | 950 | 475000
b | 7 x 2.5mm2 control cable (Genserator Voltage sensing) |  | Mtrs | 500 | 2510 | 1255000
c | 7 x 2.5mm2 control cable (Bus Voltage sensing) |  | Mtrs | 500 | 2510 | 1255000
d | 7 x 2.5mm2 control cable (Measuring current transformer) |  | Mtrs | 500 | 2510 | 1255000
e | 2 x 2.5mm2 shielded cable (Genserator Voltage control) |  | Mtrs | 500 | 2650 | 1325000
f | 2 x 2.5mm2 shielded cable (Genserator speed control) |  | Mtrs | 500 | 2650 | 1325000
g | 10 x 2.5mm2 control cable (Genserator control signal) |  | Mtrs | 500 | 3420 | 1710000
h | 10 x 2.5mm2 control cable (Breaker control signal) |  | Mtrs | 500 | 3420 | 1710000
i | 10 x 1.5mm2 control cable (MVSWG control to synch panel) |  | Mtrs | 500 | 2300 | 1150000
j | 4 x 2.5mm2 control cable (Trickle charger) |  | Mtrs | 500 | 1350 | 675000
k | 10 x 2.5mm2 control cable (Transformer control signal) |  | Mtrs | 500 | 3420 | 1710000
8 | LAGGING + CLADING FOT EXHAUST
a | Rockwool & Stainless cladding for both genset exhaust pots and line outside exhaust up to raincap |  | Nos | 5 | 2750000 | 13750000
9 | PIPE LINE CONNECTION
a | Rectangular Steel Storage Tank Signle Wall - 10,000 Litres Capacity - Inlet, Outlet, Return Line, Vent, Drain, Manhole, overflow | Fresh Oil tank | Nos | 1 | 3912957.8 | 3912957.8
b | Rectangular Steel Storage Tank Signle Wall - 5,000 Litres Capacity - Inlet, Outlet, Return Line, Vent, Drain, Manhole, overflow | Waste Oil tank | Nos | 1 | 2835900 | 2835900
c | Supply and fabrication pipings + supports for Fresh oil conection to gen-set |  | Lots | 1 | 2970000 | 2970000
d | Supply and fabrication pipings + supports for Waste oil conection to gen-set |  | Lot | 1 | 2750000 | 2750000
e | Supply and fabrication pipings + supports for Air starting conection to gen-set |  | l | 1 | 14720000 | 14720000
f | Gas Line connection  Supply, Fabricate and install gas pipeline, between the genset & its supports & final hook up to customer's gas supply point  Pickling  X-Tray Test | 5 x CG260-16 | Lot | 1 | 15750000 | 15750000
10 | EARTHING SYSTEM
a | Complete earting system with 95mm2 single pvc copper Earth cable, 20mm dia. copper earthing rods, earth pit, inspection chamber, cable lugs & clips. (Generator, Transformer, Panels, diesel tanks ) |  | Pts | 6 | 750000 | 4500000
11 | CABLE TRAYS AND ITS SUPPORTS
a | 500mm x 50mm wide Steel cable tray on ladder supports for power cable |  | Mtrs | 100 | 19500 | 1950000
b | 800mm 50mm wide Steel cable tray on ladder support for power cable |  | Mtrs | 100 | 23500 | 2350000
c | 100mm x 50mm wide Steel cable tray on ladder supports for control & communication cables |  | Mtrs | 200 | 11500 | 2300000
d | Mechanical Installation accessories for cable tray and ladder works: Tray elbows, anchor bolt M10, Unit struct 50x50mm, spring nuts, slice half tray bends,cable tray nuts etc. |  | Lot | 1 | 950000 | 950000
e | Electrical Installation Accessories: (Shrinkable hose, Cable ties, End Sleeves, Spray foam, Cable lugs, Terminal blocks, Spiral hose, shrinkable hose, saddle clip, cable connectors, lugs, Insulation tape cable markers etc.) |  | Lots | 1 | 1000000 | 1000000
12 | TRANSPORTATION
a | Transportation of men and all other necessary materials. + Accomodation |  | Lots | 1 | 4500000 | 4500000
b | Provisional sum |  | Lots | 1 | 25000000 | 25000000
13 | LABOR
a | Labour and supervisory work  Man hour / supervision for all mechanical works & Electrical works  Man hour / supervision for power laying & terminations  Man hour / supervision for control termination |  | Lot | 1 | 15000000 | 15000000
| TOTAL |  |  |  |  | 154850357.8